## TR Details
| CUSTOMER – M/s.Adani GAIMS Library-SF VRV Annexure - I : Basis Of Design | [18 empty] | R0-09.01.24
PROJECT – M/s.Adani GAIMS Library-SF VRV
System-01
SR. NO. | Space Description | Floor | Area To be Airconditioned | Total Height | False Ceiling Height | Fresh Air | Occupancy | Electrical Load |  | As per Heatload |  |  | SHF | ADP | PROPOSED INDOOR UNIT
| Area TAG |  | (Sq.Ft) | (FT) | (FT) | CFM | Nos. | Lighting Load | Eqpt. Load | Air Conditioning TR | Dehumidifier TR | CFM |  |  | IDU MODEL | TYPE | TR | CFM | QTY. | TOTAL TR | TOTAL CFM
[8 empty] | Watts | Kw
1 | SF-Area 1 | SF | 3443.2 | 9.84 | 9.84 | 564.6848 | 50 | 1 | 0 | 16.3366 | 18.9152 | 6620.3228 | 0.92738 | 50 |  | 4-Way Cassette | 2.5583 | 865 | 6 | 15.35 | 5190
2 | SF-Area 2 | SF | 1345 | 9.84 | 9.84 | 225 | 30 | 1 | 0 | 8.752 | 10.4959 | 3673.5634 | 0.92442 | 50 |  | 4-Way Cassette | 2.5583 | 865 | 4 | 10.2333 | 3460
3 | SF-Area 3 | SF | 3860.15 | 9.84 | 9.84 | 750 | 100 | 1 | 0 | 20.6655 | 22.7442 | 7960.482 | 0.88829 | 50 |  | 4-Way Cassette | 3.1833 | 1183 | 7 | 22.2833 | 8281
|  |  | 8648.35 |  |  | 1539.6848 |  |  |  | 45.7542 | 52.1553 | 18254.3683 | [6 empty] | 17 | 47.8667 | 16931
[19 empty] | ODU (HP) | 60
[19 empty] | ODU (TR) | 48
[19 empty] | DIVERSITY | 99.72%
System-02
1 | SF-Area 4 | SF | 4131.84 | 9.84 | 9.84 | 750 | 100 | 1 | 0 | 22.5848 | 25.5058 | 8927.0316 | 0.89916 | 50 |  | 4-Way Cassette | 1.6 | 812 | 11 | 17.6 | 8932
|  |  | 4131.84 |  |  | 750 |  |  |  | 22.5848 | 25.5058 | 8927.0316 | [6 empty] | 11 | 17.6 | 8932
[19 empty] | ODU (HP) | 20
[19 empty] | ODU (TR) | 16
[19 empty] | DIVERSITY | 110%
Assumtion
1 | Inside Condition : 24 Deg C , + / -1 Deg C DB | [16 empty] | 80 | HP
| RH - Around 55% | [16 empty] | 64 | TR
2 | Out Side Condition : 43 Deg C DB | [16 empty] | 110% | Diversity
3 | Lighting Load - 1.0 Watts / Sq.ft | [14 empty] | Factor 1 | 0.98 | 0 | Derated ODU TR
4 | Fresh Air - 1 Air change or 7.5cfm per person | [14 empty] | Factor 2 | 0.98 | 17.6 | Total Nominal IDU TR
5 | Equipment Load Considered 100watts / PC. | [16 empty] | 0 | IDU Performance factor
6 | Occupancy consider as per Architectural layout | [16 empty] | 0 | IDU Capacity @ diversity
7 | Exposed Glass Double Pane inside ventian blind or Roller Shade. | [16 empty] | 22.5848 | Total IDU TR as per heatload
8 | For First Floor, Floor below is consider AC & above is Considered Non AC . | [16 empty] | ok | Result
Note - Factor 1 needs to be change as per Equvivalent Piping Length & Elevation differance
Note - Factor 2 needs to be change as per indoor WBT.

## BOQ
Annexure-I - Price Schedule for the Supply of Air-conditioning Equipments
Sr No | Equipments Details | UoM | Qty | Model/Make | Rate | GST % | Amount
I | SUPPLY OF VRV X SYSTEM (COOL SYSTEM ) - R410 GAS
A | SUPPLY OF OUTDOOR UNIT
1 | 20 HP VRV OUTDOOR UNIT | Nos | 4
B | SUPPLY OF INDOOR UNIT
i) | 1 TR CONCEALED SPLIT | Nos
i) | 1.6 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 11
ii) | 2.6 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 10
iii) | 3.2 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 7
C | SUPPLY OF CORDLESS REMOTE | Nos | 28
D | SUPPLY OF REF JOINT | Nos | 27
E | SUPPLY OF ODU CONNECTOR | Nos | 4
F | SUPPLY OF MULTICONNECTING KIT FOR CONNECTIG 3 ODU | Nos | 1
Basic Amount ( Part A ) Supply Machines
GST %
Total Amount ( Part A ) Supply Machines
Payment Term:-
Delivery Time:-
Warranty period:-
Order to be Places Name :-
Annexure - II - Price Schedule for the Ancillary Job, Installation job work of Air-conditioning Equipments
Sr no | Services Details | UoM | Qty | Model/Make | Rate | GST % | Amount
I | MACHINE INSTALLAION, TESTING & COMMISSIONING OF VRV X ( COOL SYSTEM )
A | INSTALLATION OF OUTDOOR UNITS
1 | 20 HP VRV OUTDOOR UNIT | Nos | 4
B | INSTALLATION OF INDOOR UNIT
i) | 1.6 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 11
ii) | 2.6 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 10
iii) | 3.2 TR 4 WAY CASSETTE AC WITH GRILL | Nos | 7
C | INSTALLATION OF MULTICONNECTING KIT FOR CONNECTIG 3 ODU | Nos | 1
D | INSTALLATION OF REF JOINT | Nos | 27
SUB TOTAL PART (I)
II | ANCILLARY JOB
1 | SUPPLY & INSTALATION CHARGES FOR REFRIGERENT THICK HARD / SOFT COPPER PIPING BETWEEN EACH INDOOR & OUTDOOR UNITS WITH NITRILE SLEEVE. MAKE - MANDEV/MEXFLOW/HARIOM MTAL/INDOGO/RR | Mtr | 345
2 | SUPPLY & INSTALATION CHARGES FOR PVC DRAIN PIPING FOR ALL INDOOR UNIT, MAKE- SUPREME/PRINCE/FINLOEX | Mtr | 280
3 | SUPPLY & INSTALATION CHARGES FOR COMMUNICATION CABLE BETWEEN IDU TO ODU, MAKE- POLYCAB/AVOCAB/RR/FINOLEX | Mtr | 690
4 | SUPPLY & INSTALATION CHARGES FOR ODU STAND FOR VRV UNIT | Lot | 1
5 | SUPPLY & INSTALATION CHARGES FOR REFRIGERANT FOR VRV SYSTEM, MAKE- DUPONT/FREON/HONEYWELL | Lot | 1
6 | DISMANTLING CHARGES OF EXISTING CASSETTE AC | Nos | 28
7 | CHARGES FOR SCAFFOLDING | Lot | 1
8 | CHARGES FOR HYDRA/CRANE REQUIRED FOR LIFTING/SHIFTING OF OUTDOOR UNIT | Lot | 1
9 | CHARGES FOR CIVIL WORK LIKE HOLE/CORE CUTTING/JERRY WORK | Lot | 1
10 | SUPPLY & INSTALLATION CHARGES OF POWER CABLE WITH CONDUIT PIPE FOR EACH INDOOR UNIT, 3 C X 1.5 SQMM CABLE, MAKE- POLYCAB/AVOCAB/RR/FINOLEX | Mtr | 2000
11 | SUPLY & INSTALLATION CHARGES OF CABLE WITH CONDUIT PIPE FOR EARTHING 1C X 2.5 SQMM , MAKE- POLYCAB/AVOCAB/RR/FINOLEX | Mtr | 50
12 | DISMENTLING CHARGES OF EXISTING COPPER PIPE/DRAIN PIPE AND COMMUNICATION CABLE OF SPLIT AC | Lot | 1
13 | SUPLY & INSTALLATION CHARGES OF 4 C X 10 SQMM COPPER ARMOURED CABLE FOR OUTDOOR UNIT MAKE- POLYCAB/AVOCAB/RR/FINOLEX | Mtr | 300
14 | SUPPLY & INSTALLATION CHARGES OF GI LADDER TYPE TOP COVER CABLE TRAY OF 300 MM X 75 MM SIZE (FOR LAYING OF EXPOSED COPPER PIPE ON TERRACE ) | Mtr | 60
15 | SUPPLY & INSTALLATION OF 63 AMP 4 POLE C -CURVED TYPE RCBO FOR 20 HP ODU UNIT | Nos | 4
16 | SUPPLY & INSTALLATION OF (FOR AREA - 1), 8-WAY SINGLE PHASE DISTRIBUTION BOX WITH 25 AMP X 1NOS INCOMER MCB, 6 AMP X 6 NOS OUTGOING SP MCB, C-CURVED WITH EARTHJING STRIP ARRANGEMENT | Nos | 1
17 | SUPPLY & INSTALLATION OF (FOR AREA - 2), 14-WAY SINGLE PHASE DISTRIBUTION BOX WITH 50 AMP X 1NOS INCOMER MCB, 6 AMP X 11 NOS OUTGOING SP MCB, C-CURVED WITH EARTHJING STRIP ARRANGEMENT | Nos | 1
18 | SUPPLY & INSTALLATION OF FOR AREA - 30, 14-WAY SINGLE PHASE DISTRIBUTION BOX WITH 50 AMP X 1NOS INCOMER MCB, 6 AMP X 11 NOS OUTGOING SP MCB, C-CURVED WITH EARTHJING STRIP ARRANGEMENT | Nos | 1
19 | SUPPLY & INSTALLATION OF 25 AMP X 1NOS, 50 AMP X 2 NOS 2 POLE MCB FEEDER FOR INDOOR UNIT 3 NOS DISCTRIBUTION BOX, C-CURVED MCB | Nos | 1
20 | SUPPLY & INSTALLATION OF 3 C X 4 SQMM COPPER CABLE WITH CONDUIT PIPE FOR AREA -1 | Mtr | 150
21 | SUPPLY & INSTALLATION OF 3 C X 10 SQMM COPPER CABLE WITH CONDUIT PIPE FOR AREA-2 & 3 | Mtr | 300
22 | SUPPLY & INSTALLATION OF ALL ELECTRICAL FITTING ACCESSORIES LIKE LUGS/GLAND/JOINTS. | Lot | 1
23 | SUPPLY & INSTALLATION CHARGES OF PERFORATED TYPE TOP COVER CABLE TRAY OF 300 MM X 75 SIZE (FOR LAYING OF ARMOURED COPPER CABLE ) | Mtr | 150
Basic Amount ( Part - B ) Installation Works
GST %
Total Amount ( Part - B ) Installation works
GRAND Total (Part - A+B) with GST
Payment Term:-
Work Completion Days:-
Warranty period:-
Order to be Places Name :-
Consider Below Points also
1 | Type of refrigerant of VRV system. - R410 Gas
2 | Copper pipe size, thickness and make. - Mexflow/Mandev/RR/Indigo/Hariom metal 18 G thickness.
3 | PVC drain pipe size - 32 mm PVC pipe
4 | Insulation type, thickness - 19 mm and 13 mm thick nitrile class o insulation
5 | Exposed to sky area Insulation specifications. - 19 mm and 13 mm thick class o nitrile insulation with white tap
6 | G.I Cable tray with TOP cover required.- Yes